## Calc
Vortex Enclosure Cooler - Sizing & Selection Worksheet
Enclosure Cooler Recommendation | [6 empty] | Input cabinet information below and the recommendations will update
No match found. Please check data.
Height (in.)
Width (in.) | [5 empty] | Square Feet of Enclosure |  | 0
Depth (in.)
Compressed Air Inlet Temperature, °F | [5 empty] | Compressed Air Pressure, psig
NEMA Rating required
Thermostat Type |  |  | Electric
Noise level |  |  | Standard
Current Temperature Inside Cabinet, °F |  |  |  |  | Current Ambient Temperature, °F |  |  | Delta T °F | 0
Dissipated Heat, in Watts |  |  |  |  | Additional BTUs | 0
Desired Temperature Inside Cabinet, °F |  |  |  |  | Worst Case Ambient Temp, °F |  |  | Delta T °F | 0
Temperature rise due to solar radiation, if enclosure is exposed to direct sunlight
Number |  | Cabinet Color |  |  | Approx. Temp Rise |  | If the cabinet is exposed to direct sunlight, enter the number that corresponds to the color that matches the cabinet. If not exposed to direct sunlight, leave this box blank.
1 |  | White |  |  | 4
2 |  | Cream |  |  | 7
3 |  | Yellow |  |  | 9
4 |  | Light Gray |  |  | 14
5 |  | Medium Gray |  |  | 22
6 |  | Dark Gray |  |  | 25
7 |  | Black |  |  | 27 |  | Color Number
8 |  | National Aluminum or |  |  | 14
Stainless Steel
| Total Delta T °F : |  |  |  |  | 0
If fan cooled:
Temperature of air entering enclosure °F
*Temperature of air exiting enclosure °F
Fan Rating, SCFM
| Additional BTUs provided by fans: |  |  |  |  | 0
Total Heat Load of Cabinet : | [5 empty] | 0 | BTU per hour
Rating of Vortex Cooler required : | [5 empty] | 0 | SCFM
Enclosure Cooler Recommendation
No match found. Please check data.

## Calc references (hidden)
NEMA Rating
4
4X
12
HazLoc
If not HazLoc | If NEMA HazLoc
Mechanical | Mechanical
Electric
None
If Mechanical | If Electric/None | If HazLocMechanical
Quiet | Standard | Quiet
Standard

## LookupTable (hidden)
Rating Required | 0 |  | RECOMMENDATION | #N/A
RxTxN value | ElectricStandard |  | Cooling Capacity | #N/A
Brand | #N/A
NOTE: Make sure that Air Consumption column is sorted in ascending order
Rating | Thermostat Option | Noise Level | RxTxN | Air Consumption, SCFM | Cooling Capacity, BTU/hr | Brand | Item # | BxI
12 | Electric | Standard | 12ElectricStandard | 7 | 400 | Vortex Cooler | 750 | Vortex Cooler - 750
12 | None | Standard | 12NoneStandard | 7 | 400 | Vortex Cooler | 760 | Vortex Cooler - 760
HazLoc | Mechanical | Quiet | HazLocMechanicalQuiet | 15 | 900 | Hazardous Location Vortex A/C | 7515 | Hazardous Location Vortex A/C - 7515
4 | Mechanical | Standard | 4MechanicalStandard | 15 | 900 | Panel Guard | 770-15H | Panel Guard - 770-15H
12 | Mechanical | Quiet | 12MechanicalQuiet | 15 | 900 | Vortex A/C | 7615 | Vortex A/C - 7615
4 | Mechanical | Quiet | 4MechanicalQuiet | 15 | 900 | Vortex A/C | 7715 | Vortex A/C - 7715
4X | Mechanical | Quiet | 4XMechanicalQuiet | 15 | 900 | Vortex A/C | 7715 | Vortex A/C - 7715
12 | None | Standard | 12NoneStandard | 15 | 900 | Vortex Cooler | 730 | Vortex Cooler - 730
12 | Electric | Standard | 12ElectricStandard | 15 | 900 | Vortex Cooler | 740 | Vortex Cooler - 740
4 | None | Standard | 4NoneStandard | 15 | 900 | Vortex Cooler | 737 | Vortex Cooler - 737
4 | Electric | Standard | 4ElectricStandard | 15 | 900 | Vortex Cooler | 747 | Vortex Cooler - 747
4X | None | Standard | 4XNoneStandard | 15 | 900 | Vortex Cooler | 737SS | Vortex Cooler - 737SS
4X | Electric | Standard | 4XElectricStandard | 15 | 900 | Vortex Cooler | 747SS | Vortex Cooler - 747SS
HazLoc | Mechanical | Quiet | HazLocMechanicalQuiet | 25 | 1500 | Hazardous Location Vortex A/C | 7525 | Hazardous Location Vortex A/C - 7525
4 | Mechanical | Standard | 4MechanicalStandard | 25 | 1500 | Panel Guard | 770 | Panel Guard - 770
12 | Mechanical | Quiet | 12MechanicalQuiet | 25 | 1500 | Vortex A/C | 7625 | Vortex A/C - 7625
4 | Mechanical | Quiet | 4MechanicalQuiet | 25 | 1500 | Vortex A/C | 7725 | Vortex A/C - 7725
4X | Mechanical | Quiet | 4XMechanicalQuiet | 25 | 1500 | Vortex A/C | 7725 | Vortex A/C - 7725
12 | None | Standard | 12NoneStandard | 25 | 1500 | Vortex Cooler | 780 | Vortex Cooler - 780
12 | Electric | Standard | 12ElectricStandard | 25 | 1500 | Vortex Cooler | 790 | Vortex Cooler - 790
4X | None | Standard | 4XNoneStandard | 25 | 1500 | Vortex Cooler | 787SS | Vortex Cooler - 787SS
4X | Electric | Standard | 4XElectricStandard | 25 | 1500 | Vortex Cooler | 797SS | Vortex Cooler - 797SS
4 | None | Standard | 4NoneStandard | 28 | 1700 | Vortex Cooler | 787 | Vortex Cooler - 787
4 | Electric | Standard | 4ElectricStandard | 28 | 1700 | Vortex Cooler | 797 | Vortex Cooler - 797
HazLoc | Mechanical | Quiet | HazLocMechanicalQuiet | 35 | 2500 | Hazardous Location Vortex A/C | 7535 | Hazardous Location Vortex A/C - 7535
4 | Mechanical | Standard | 4MechanicalStandard | 35 | 2500 | Panel Guard | 770-35H | Panel Guard - 770-35H
12 | Mechanical | Quiet | 12MechanicalQuiet | 35 | 2500 | Vortex A/C | 7635 | Vortex A/C - 7635
4 | Mechanical | Quiet | 4MechanicalQuiet | 35 | 2500 | Vortex A/C | 7735 | Vortex A/C - 7735
4X | Mechanical | Quiet | 4XMechanicalQuiet | 35 | 2500 | Vortex A/C | 7735 | Vortex A/C - 7735
12 | None | Standard | 12NoneStandard | 35 | 2500 | Vortex Cooler | 785 | Vortex Cooler - 785
12 | Electric | Standard | 12ElectricStandard | 35 | 2500 | Vortex Cooler | 795 | Vortex Cooler - 795
4 | None | Standard | 4NoneStandard | 35 | 2500 | Vortex Cooler | 787-35H | Vortex Cooler - 787-35H
4 | Electric | Standard | 4ElectricStandard | 35 | 2500 | Vortex Cooler | 797-35H | Vortex Cooler - 797-35H
4X | None | Standard | 4XNoneStandard | 35 | 2500 | Vortex Cooler | 787SS-35H | Vortex Cooler - 787SS-35H
4X | Electric | Standard | 4XElectricStandard | 35 | 2500 | Vortex Cooler | 797SS-35H | Vortex Cooler - 797SS-35H
HazLoc | Mechanical | Quiet | HazLocMechanicalQuiet | 70 | 5000 | Hazardous Location Vortex A/C | 7570 | Hazardous Location Vortex A/C - 7570
12 | Mechanical | Quiet | 12MechanicalQuiet | 70 | 5000 | Vortex A/C | 7670 | Vortex A/C - 7670
4 | Mechanical | Quiet | 4MechanicalQuiet | 70 | 5000 | Vortex A/C | 7770 | Vortex A/C - 7770
4X | Mechanical | Quiet | 4XMechanicalQuiet | 70 | 5000 | Vortex A/C | 7770 | Vortex A/C - 7770
12 | None | Standard | 12NoneStandard | 70 | 5000 | Vortex Cooler | 7870 | Vortex Cooler - 7870
12 | Electric | Standard | 12ElectricStandard | 70 | 5000 | Vortex Cooler | 7970 | Vortex Cooler - 7970
4 | None | Standard | 4NoneStandard | 70 | 5000 | Vortex Cooler | 7875 | Vortex Cooler - 7875
4 | Electric | Standard | 4ElectricStandard | 70 | 5000 | Vortex Cooler | 7975 | Vortex Cooler - 7975
4X | None | Standard | 4XNoneStandard | 70 | 5000 | Vortex Cooler | 7875SS | Vortex Cooler - 7875SS
4X | Electric | Standard | 4XElectricStandard | 70 | 5000 | Vortex Cooler | 7975SS | Vortex Cooler - 7975SS

## Metric (hidden)
Item # | Cooling Capacity, Watts | Rating | Thermostat Option | Noise Level | Includes Filter & Ducting Kit? | Air Consumption, SLPM | Brand
711 | 1365 | NEMA 12 | None | Standard | No | 190 | Vortex Coolers
750 | 1365 | NEMA 12 | Electric | Standard | Yes | 190 | Vortex Coolers
760 | 1365 | NEMA 12 | None | Standard | Yes | 190 | Vortex Coolers
730 | 3070 | NEMA 12 | None | Standard | Yes | 425 | Vortex Coolers
737 | 3070 | NEMA 4 | None | Standard | Yes | 425 | Vortex Coolers
740 | 3070 | NEMA 12 | Electric | Standard | Yes | 425 | Vortex Coolers
747 | 3070 | NEMA 4 | Electric | Standard | Yes | 425 | Vortex Coolers
7015 | 3070 | NEMA 4/4X | Mechanical | Quiet | No | 425 | Vortex A/C
7115 | 3070 | NEMA 12 | Mechanical | Quiet | No | 425 | Vortex A/C
7215 | 3070 | Class 1, Div 2 | Mechanical | Quiet | No | 425 | Hazardous Location Vortex A/C
7515 | 3070 | Class 1, Div 2 | Mechanical | Quiet | Yes | 425 | Hazardous Location Vortex A/C
7615 | 3070 | NEMA 12 | Mechanical | Quiet | Yes | 425 | Vortex A/C
7715 | 3070 | NEMA 4/4X | Mechanical | Quiet | Yes | 425 | Vortex A/C
701-15H | 3070 | NEMA 4 | Mechanical | Standard | No | 425 | Panel Guard
721-15H | 3070 | NEMA 12 | None | Standard | No | 425 | Vortex Coolers
727-15H | 3070 | NEMA 4 | None | Standard | No | 425 | Vortex Coolers
727SS-15H | 3070 | NEMA 4X | None | Standard | No | 425 | Vortex Coolers
737SS | 3070 | NEMA 4X | None | Standard | Yes | 425 | Vortex Coolers
747SS | 3070 | NEMA 4X | Electric | Standard | Yes | 425 | Vortex Coolers
770-15H | 3070 | NEMA 4 | Mechanical | Standard | Yes | 425 | Panel Guard
701 | 5115 | NEMA 4 | Mechanical | Standard | No | 708 | Panel Guard
721 | 5115 | NEMA 12 | None | Standard | No | 708 | Vortex Coolers
770 | 5115 | NEMA 4 | Mechanical | Standard | Yes | 708 | Panel Guard
780 | 5115 | NEMA 12 | None | Standard | Yes | 708 | Vortex Coolers
790 | 5115 | NEMA 12 | Electric | Standard | Yes | 708 | Vortex Coolers
797 | 5115 | NEMA 4 | Electric | Standard | Yes | 708 | Vortex Coolers
7025 | 5115 | NEMA 4/4X | Mechanical | Quiet | No | 708 | Vortex A/C
7125 | 5115 | NEMA 12 | Mechanical | Quiet | No | 708 | Vortex A/C
7225 | 5115 | Class 1, Div 2 | Mechanical | Quiet | No | 708 | Hazardous Location Vortex A/C
7525 | 5115 | Class 1, Div 2 | Mechanical | Quiet | Yes | 708 | Hazardous Location Vortex A/C
7625 | 5115 | NEMA 12 | Mechanical | Quiet | Yes | 708 | Vortex A/C
7725 | 5115 | NEMA 4/4X | Mechanical | Quiet | Yes | 708 | Vortex A/C
787SS | 5115 | NEMA 4X | None | Standard | Yes | 708 | Vortex Coolers
797SS | 5115 | NEMA 4X | Electric | Standard | Yes | 708 | Vortex Coolers
727 | 5798 | NEMA 4 | None | Standard | No | 793 | Vortex Coolers
787 | 5798 | NEMA 4 | None | Standard | Yes | 793 | Vortex Coolers
727SS | 5798 | NEMA 4X | None | Standard | No | 793 | Vortex Coolers
785 | 8525 | NEMA 12 | None | Standard | Yes | 991 | Vortex Coolers
795 | 8525 | NEMA 12 | Electric | Standard | Yes | 991 | Vortex Coolers
7035 | 8525 | NEMA 4/4X | Mechanical | Quiet | No | 991 | Vortex A/C
7135 | 8525 | NEMA 12 | Mechanical | Quiet | No | 991 | Vortex A/C
7235 | 8525 | Class 1, Div 2 | Mechanical | Quiet | No | 991 | Hazardous Location Vortex A/C
7535 | 8525 | Class 1, Div 2 | Mechanical | Quiet | Yes | 991 | Hazardous Location Vortex A/C
7635 | 8525 | NEMA 12 | Mechanical | Quiet | Yes | 991 | Vortex A/C
7735 | 8525 | NEMA 4/4X | Mechanical | Quiet | Yes | 991 | Vortex A/C
701-35H | 8525 | NEMA 4 | Mechanical | Standard | No | 991 | Panel Guard
721-35H | 8525 | NEMA 12 | None | Standard | No | 991 | Vortex Coolers
727-35H | 8525 | NEMA 4 | None | Standard | No | 991 | Vortex Coolers
727SS-35H | 8525 | NEMA 4X | None | Standard | No | 991 | Vortex Coolers
770-35H | 8525 | NEMA 4 | Mechanical | Standard | Yes | 991 | Panel Guard
787-35H | 8525 | NEMA 4 | None | Standard | Yes | 991 | Vortex Coolers
787SS-35H | 8525 | NEMA 4X | None | Standard | Yes | 991 | Vortex Coolers
797-35H | 8525 | NEMA 4 | Electric | Standard | Yes | 991 | Vortex Coolers
797SS-35H | 8525 | NEMA 4X | Electric | Standard | Yes | 991 | Vortex Coolers
7070 | 17050 | NEMA 4/4X | Mechanical | Quiet | No | 1982 | Vortex A/C
7170 | 17050 | NEMA 12 | Mechanical | Quiet | No | 1982 | Vortex A/C
7270 | 17050 | Class 1, Div 2 | Mechanical | Quiet | No | 1982 | Hazardous Location Vortex A/C
7570 | 17050 | Class 1, Div 2 | Mechanical | Quiet | Yes | 1982 | Hazardous Location Vortex A/C
7670 | 17050 | NEMA 12 | Mechanical | Quiet | Yes | 1982 | Vortex A/C
7770 | 17050 | NEMA 4/4X | Mechanical | Quiet | Yes | 1982 | Vortex A/C
7870 | 17050 | NEMA 12 | None | Standard | Yes | 1982 | Vortex Coolers
7875 | 17050 | NEMA 4 | None | Standard | Yes | 1982 | Vortex Coolers
7970 | 17050 | NEMA 12 | Electric | Standard | Yes | 1982 | Vortex Coolers
7975 | 17050 | NEMA 4 | Electric | Standard | Yes | 1982 | Vortex Coolers
7875SS | 17050 | NEMA 4X | None | Standard | Yes | 1982 | Vortex Coolers
7975SS | 17050 | NEMA 4X | Electric | Standard | Yes | 1982 | Vortex Coolers